## Checklist
Minimum Interconnection Request
Submission Requirements
Revision 1.0
Effective Date: 05/15/2026
The items listed below are required for a valid Interconnection Request submission. WWD will review submissions for completeness in accordance with the LGIP. Incomplete submissions may be subject to deficiency notice, cure requirements, or withdrawal from the Cluster Study Process if deficiencies are not timely resolved.
1. | FALSE | $10,000 Application fee (non-refundable)
2. | FALSE | $30,000 Cluster Study deposit
3. | FALSE | Completed Appendix 1 (see "Appendix 1" excel tab)
4. | FALSE | Completed Attachment A to Appendix 1 (see "Attachment A" and "SCD Table" excel tabs)
5. | FALSE | Site Drawing (.kmz)
6. | FALSE | Single Line Diagram
7. | FALSE | Load Flow Model (.epc)
8. | FALSE | Dynamic Model (.dyd)
9. | FALSE | Reactive Power capability document
10 | FALSE | Evidence of Site Control
11 | FALSE | Evidence of CEQA

## Appendix 1
Interconnection Request
1. | The undersigned Inteconnection Customer submits this request to interconnect its Generating
Facility with the Westlands Water District ("WWD") Transmission System (check only one):
| FALSE | Queue Cluster Process (deliverable/capacity)
| FALSE | Queue Cluster Process (energy only)
2. | This Interconnection Request is for (check only one):
| FALSE | A proposed new Generating Facility
| FALSE | An increase in the generating capacity or a Material Modification of an existing
Generating Facility.
3. | Interconnection Customer provides the following information:
| a. | Address or location, including the county, of the proposed new Generating Facility site or,
in the case of an existing Generating Facility, the name and specific location, including the
county, of the existing Generating Facility;
Project Name:
Project Location:
Street Address:
City:
County:
State:
Zip Code:
GPS Coordinates (decimal format):
|  |  |  | Latitude: |  |  |  | Longitude:
| b. | Provide the following project megawatt values:
If project is an increase to an existing project, provide values based on the MW increase only.
Interconnection Service Capacity must be between 250 MW and 1,150 MW.
|  | Total Generating Facility Gross Capacity: | [7 empty] | MVA
This value equals the total installed MW capacity at unity power factor
|  | Total Generating Facility Gross Output: | [7 empty] | MW
Gross output achieving desired net MW at POI described below
|  | Generating Facility Auxiliary Load: | [7 empty] | MW
|  | Maximum Net Megawatt Electrical Output: | [7 empty] | MW
This is for a proposed new Generating Facility. Total Generating Facility Gross Output less
Generating Facility Auxiliary Load
OR
|  | Net Megawatt Increase: | [7 empty] | MW
This is for an increase or Material Modification to an existing Generating Facility, Total
Generating Facility Gross Output less Generating Facility Auxiliary Load
|  | Anticipated losses between the Generating Facility and POI: | [11 empty] | MW
Include all transformer and line losses between the generating units and the POI
|  | Requested Interconnection Service Capacity (Desired Net MW at POI): | [11 empty] | MW
Maximum Net Megawatt Electrical Output less Anticipated Losses
This MW value is the pro rata basis for cost allocations of Network Upgrades except short
circuit related Network Upgrades in the interconnection studies. This is the value that will
appear in the WWD interconnection queue.
Provide a descrioption of any control scheme which will be installed to ensure that the
requested Interconnection Service Capacity does not exceed the above desired value.
| c. | Type of project (i.e., gas turbine, solar, battery, etc.) and general descroption of the
equipment configuration (if more than one type is chosen include gross installed MW for
each). Note: if project is an increase to an existing project, provide values based on the MW
increase only.
|  | Generation Type |  |  | Fuel Type |  | Megawatts |  |  | Co-location |  | Hybrid
|  | Gen Technology |  |  | Gen Type |  |  |  |  | FALSE | Co-Located | FALSE | Hybrid
|  | Gen Technology |  |  | Gen Type |  |  |  |  | FALSE | Co-Located | FALSE | Hybrid
General Description of the equipment configuration (e.g. number, size, type, etc.):
| d. | Proposed In-Service Date (first date transmission is needed to the facility), Trial Operation
Commencement Date and Commercial Operation Date in MM/DD/YYY format and Term
of Service (dates must be sequential, proposed Commercial Operation Date may not be
more than seven (7) years from date of application):
(MM/DD/YYYY)
Proposed In-Service Date:
Proposed Initial Synchronization Date:
Proposed Commercial Operation Date:
Proposed Term of Service (years):
| e. | Name, address, telephone number, and e-mail address of Interconnection Customer's
contact person (primary person who will be contacted):
First Name:
Last Name:
Title:
Company Name:
Street Address:
City:
State:
Zip Code:
Phone Number:
Email Address:
| f. | Proposed Point of Interconnection: [choose from dropdowns]
|  | Substation: |  |  | Substation Name |  |  |  | Point of Interconnection
|  | Voltage Level: |  |  | Voltage Level | kV
| g. | Interconnection Customer Data (set forth in Attachment A):
4. | Applicable deposit amount made payable to WWD
|  | • | Required deposits shall be submitted in accordance with payment instructions provided by WWD for the applicable Cluster Request Window, using one or more approved payment methods.
|  | • | All required deposits must be received by WWD no later than the close of the applicable Cluster Request Window and must clearly reference the project name and any required identifying information.
|  | • | Detailed payment instructions will be published by WWD prior to opening the Cluster Request Window.
5. | Evidence of Site Control as specified in the LGIP.
| a. | Type of Site Control Provided:
|  | FALSE | Proof of Ownership (Deed)
|  | FALSE | Lease Agreement
|  | FALSE | Option to Purchase
|  | FALSE | Option to Lease
|  | FALSE | Development Agreement
|  | FALSE | Other? Please Explain:
| b. | Is Site Control granted to the Interconnection Customer (i.e. to the same entity with the
same name) identified in Section 9 of this Interconnection Request?
|  | FALSE | Yes
|  | FALSE | No. Please explain the relationship between entities.
| c. | Term of Agreement: | [10 empty] | Years
| d. | Term of Option (if applicable): | [10 empty] | Years
| e. | Total acreage acquired or reserved for project site: | [10 empty] | Acres
| f. | Acreage owned by Westlands Water District (if applicable): | [10 empty] | Acres
|  | Minimum acreage required based on Generating Facility type(s): | [8 empty] | 0 | Acres
Note: Automatically calculated based on information entered above.
Photovoltaic = 6 Acres / MW; Energy Storage (Battery) = 0.06 Acres / MW
|  | Minimum Site Control Required (90%) | [8 empty] | 0%
Note: Automatically calculated based on information entered above.
|  | Site Control Compliance Status | [8 empty] | N/A
Note: Automatically calculated based on information entered above.
6. | Evidence of CEQA as specified in the LGIP.
| a. | CEQA Lead Agency:
| b. | Please describe the status of the CEQA documents and expected date of completion:
Expected Date of Completion:
Status of the CEQA Documents:
| c. | If the CEQA document has been completed, please provide the name of the document and
the State Clearinghouse number, if available:
Name:
State Clearinghouse Number:
7. | This Interconnection Request shall be submitted as indicated below:
Submission instructions, including any required registration steps, submission portal access, and contact information, will be published by WWD prior to opening the applicable Cluster Request Window
Interconnection Requests must be submitted in accordance with the published WWD submission instructions for the applicable Cluster Request Window.
Interconnection Customers are responsible for ensuring that all required application materials, certifications, and supporting documents are properly submitted by the applicable deadline.
8. | This Interconnection Request if submitted by:
Legal name of the Interconnection Customer:
Punctuation and spelling of legal name must match Secretary of State document exactly
State of Origin for Secretary of State Document:
Name of Parent Company (if applicable):
Your electronic signature below certifies that the information contained in this Interconnection Request is true and correct to the best of the Interconnection Customer’s knowledge.
FALSE
First Name:
Last Name:
Title:
Date (MM/DD/YYYY):

## Attachment A
0
Item # |  |  |  | UNITS
| I. Overall Project MW Information | [12 empty] | Calculated values for validation. Do not enter here.
I.1 | Total Generating Facility gross capacity |  |  | MVA | 0
I.2 | Total Generating Facility gross output |  |  | MW |  | The gross MW output to achieve requested MW at POI | [7 empty] | 0
I.3 | Generating Facility Auxiliary Load |  |  | MW
I.4 | Project net capacity at Generating Facility |  |  | MW | 0
I.5 | Anticipated Losses between the Generating Facility and POI |  |  | MW |  | Include all transformer and line losses between the generating units and the POI at total Generating Facility gross output as calculated by the power flow model in .epc file
I.6 | Desired net output at POI |  |  | MW | 0 | must match MW value derived from power flow model in .epc file
I.7 | Standby Load when Generating Facility is off-line |  |  | MW
I.8 | For combined cycle plants, specify the plant net output capacity for an outage of the steam turbine or an outage of a single combustion turbine |  |  | MW
II. Individual Generating Facility Characteristics
II.1 | Generating Facility Name |  |  |  | Gen Type1 | Gen Type2 | Gen Type3 | Gen Type4 | Gen Type5 | Gen Type6 | Gen Type7 | Gen Type8 | Gen Type9
II.2 | Technology | [12 empty] | 0
II.3 | Type (Scroll to the right for help info) | [12 empty] | 1
II.4 | Manufacturer | [12 empty] | 1
II.5 | Model Name | [12 empty] | 1
II.6 | Model Number | [12 empty] | 0 | not required
II.7 | Version (if applicable) | [12 empty] | 0 | not required
II.8 | Year Manufactured | [12 empty] | 0 | not required
II.9 | Number of Individual Generators or Inverters | [12 empty] | 1
II.10 | Nominal Terminal Voltage |  |  | kV | [9 empty] | 1
II.11 | Expected average high ambient temperature for the site |  |  | ⁰C | [9 empty] | 1
II.12 | Individual generator rated MVA at the temperature above |  |  | MVA | [9 empty] | 1
II.13 | Individual generator rated MW at the temperature above |  |  | MW | [9 empty] | 1
II.14 | Individual generator power factor at rated MW | [12 empty] | 0 | calculated
II.15 | Individual generator power factor regulation range at rated MW output |  | Leading (-) | [10 empty] | 1
II.16 |  |  | Lagging (+) | [10 empty] | 1
II.17 | Generator Voltage Regulation Range (+/-) |  |  | % | [9 empty] | 1
II.18 | Phase | [12 empty] | 1
II.19 | Connection | [12 empty] | 1
II.20 | ACTION REQUIRED: |  | Please submit generator reactive capability curves
III. Synchronous Generator Information
| A. Generator | [12 empty] | 0 | calculation
III.1 | Rated Generator speed |  |  | RPM | [9 empty] | 1
III.2 | Generator Efficiency at Rated Load |  |  | % | [9 empty] | 1
III.3 | Moment of Inertia (including prime mover) | [12 empty] | 1
III.4 | Inertia Time Constant (on machine base) H (Sec or MJ/MVA) |  |  | MJ/MVA | [9 empty] | 1
III.5 | SCR (Short-Circuit Ratio – the ratio of the field current required for rated open-circuit voltage to the field current required for rated short-circuit current | [12 empty] | 1
III.6 | [13 empty] | 0 | skip
III.7 | Rated Hydrogen Cooling Pressure (Steam Units only) |  |  | PSIG | [9 empty] | 0 | skip
III.8 | Dynamic Model Name | [12 empty] | 1
III.9 |  | If other, specify the model name and reason to use non-WECC approved model | [11 empty] | 2 | 45 | Other (Explain Below)
[14 empty] | 0 | skip
III.10 | ACTION REQUIRED: |  | Please submit a plot of generator terminal voltage versus field current that shows the air gap line, the open-circuit saturation curve, and the saturation curve at full load and rated power factor | [10 empty] | 0 | skip
[14 empty] | 0 | skip
| B. Excitation for Each Generator | [12 empty] | 1 | this section is required if unit or plant > 75MVA
III.11 | Manufacture | [12 empty] | 1
III.12 | For exciter type, please choose from 1 to 9 below or describe the specific excitation system. | [12 empty] | 1
III.13 |  | Other? - Please Specify: | [11 empty] | 2 | 52 | Other? (Specify):
III.14 | Excitation system response ratio |  |  | ASA | [9 empty] | 1
III.15 | Full load rated exciter output voltage |  |  | V | [9 empty] | 1
III.16 | Maximum exciter output voltage (ceiling voltage) |  |  | V | [9 empty] | 1
III.17 | Other comments regarding the excitation system? | [12 empty] | 0 | skip
[14 empty] | 0 | skip
III.18 | ACTION REQUIRED: |  | Please submit a copy of the block diagram of the excitation system from its instruction manual | [10 empty] | 0 | skip
[14 empty] | 0 | skip
III.19 | C. Power System Stabilizer for Each Generator | [12 empty] | 1 | this section is required if unit > 75MVA or unit > 30MVA and plant > 75 MVA
III.20 | Manufacturer | [12 empty] | 1
III.21 | Is the PSS digital or analog: | [12 empty] | 1
III.22 | Note the input signal source for the PSS | [12 empty] | 1
III.23 |  | Other? - Please Specify: | [11 empty] | 2 | 64 | Other (Explain Below)
III.24 | Other comments regarding the PSS? | [12 empty] | 0 | skip
| ACTION REQUIRED: |  | Please attach a copy of a block diagram of the PSS from the PSS Instruction Manual and the correspondence between dial settings and the time constants or PSS gain | [10 empty] | 0
0
| D. Turbine-Governor for Each Generator | [12 empty] | 1 | this section is required if unit or plant > 75MVA
III.24 | Turbine Type | [12 empty] | 1
III.25 | Turbine manufacturer | [12 empty] | 1
III.26 | Maximum turbine power output |  |  | MW | [9 empty] | 1
III.27 | Minimum turbine power output (while on line) |  |  | MW | [9 empty] | 1
III.28 | Governor Droop setting (speed regulation) | [12 empty] | 1
III.29 | Is the governor mechanical-hydraulic or electro-hydraulic? (electro-hydraulic governors have an electronic speed sensor and transducer) | [12 empty] | 1
[14 empty] | 0 | skip
III.30 | Other comments regarding the turbine governor system: | [12 empty] | 0 | skip
[14 empty] | 0 | skip
| E. Steam, gas or combined-cycle turbines: | [12 empty] | 0 | calculation
III.31 | If steam or combined-cycle, does the turbine system have a reheat process (i.e., both high and low pressure turbines)? | [12 empty] | 1
[14 empty] | 0 | skip
| If steam with reheat process, or if combined-cycle, indicate the percent of full load power produced by each turbine: | [12 empty] | 0 | skip
[14 empty] | 0 | skip
III.32 |  | Low pressure turbine or gas turbine |  | % | [9 empty] | 2 | 81 | Yes
III.33 |  | High pressure turbine or steam turbine |  | % | [9 empty] | 2 | 81 | Yes
| F. Hydro turbines: | [12 empty] | 0 | calculation
III.34 | Turbine efficiency at rated load |  |  | % | [9 empty] | 1
III.35 | Length of penstock |  |  | Feet | [9 empty] | 1
III.36 | Average cross-sectional area of the penstock |  |  | Feet2 | [9 empty] | 1
III.37 | Typical maximum head (vertical distance from the bottom of the penstock, at the gate, to the water level) |  |  | Feet | [9 empty] | 1
1
III.38 | Water supply | [12 empty] | 1
III.39 | Water flow rate at the typical maximum head |  |  | Ft3/Sec | [9 empty] | 1
III.40 | Average energy rate |  |  | kWh/ Acre-Ft | [9 empty] | 1
III.41 | Estimated yearly energy production |  |  | kWh/ Year | [9 empty] | 1
| G. Short Circuit Data | [12 empty] | 0 | calculation
III.42 | X"1 – positive sequence subtransient reactance (saturated) |  |  | p.u** | [9 empty] | 1
III.43 | X"1 – positive sequence subtransient reactance (unsaturated) |  |  | p.u** | [9 empty] | 1
III.44 | X2 – negative sequence reactance |  |  | p.u** | [9 empty] | 1
III.45 | X0 – zero sequence reactance |  |  | p.u** | [9 empty] | 1
III.46 | Generator Grounding | [12 empty] | 1
III.47 |  | If grounded through impedance, please enter: | R: | ohms | [9 empty] | 2 | 104 | Grounded through Impedance
III.48 |  |  | X: | ohms | [9 empty] | 2 | 104 | Grounded through Impedance
III.49 | ** On generator MVA base and nominal line voltage (kV) Base
IV. Induction Machine Information (Individual Generator Data)
| Induction Machine Information | [12 empty] | 0 | calculation
IV.1 | Moment of Inertia (including prime mover) | [12 empty] | 1
IV.2 | Do you wish reclose blocking? | [12 empty] | 1
| Note: Sufficient capacitance may be on the line now, or in the future, and the generator may self-excite unexpectedly. | [12 empty] | 0 | skip
| Fill out the following for wind generators type 1, 2 or 3 (for Type 4 Wind Generators, skip to section V.) | [12 empty] | 0 | skip
IV.3 | Turbine Type | [12 empty] | 1
IV.4 | Average Site Elevation |  |  | Feet | [9 empty] | 1
IV.5 | Field Volts |  |  | Volt | [9 empty] | 1
IV.6 | Field Amperes |  |  | Amp | [9 empty] | 1
IV.7 | Motoring Power |  |  | MW | [9 empty] | 1
IV.8 | Neutral Grounding Resistor (in applicable) |  |  | ohm | [9 empty] | 1
IV.9 | I22t of K (Heating Time Constant) |  |  | sec | [9 empty] | 1
IV.10 | Rotor Resistance |  |  | ohm | [9 empty] | 1
IV.11 | Stator Resistance |  |  | ohm | [9 empty] | 1
IV.12 | Stator Reactance |  |  | ohm | [9 empty] | 1
IV.13 | Magnetized Reactance |  |  | ohm | [9 empty] | 1
IV.14 | Short Circuit Reactance |  |  | ohm | [9 empty] | 1
IV.15 | Exciting Current |  |  | amp | [9 empty] | 1
IV.16 | Temperature Rise | [12 empty] | 1
IV.17 | Frame Size | [12 empty] | 1
IV.18 | Design Letter | [12 empty] | 1
IV.19 | Reactive Power Required (No Load) |  |  | kVARS | [9 empty] | 1
IV.20 | Reactive Power Required (Full Load) |  |  | kVARS | [9 empty] | 1
IV.21 | Total Rotating Inertial I (Per Unit on 100 MVA Base) |  |  | p.u | [9 empty] | 1
| Short Circuit Data | [12 empty] | 0 | skip
IV.22 | X"1 – positive sequence subtransient reactance (saturated) |  |  | p.u** | [9 empty] | 1
IV.23 | X"1 – positive sequence subtransient reactance (unsaturated) |  |  | p.u** | [9 empty] | 1
IV.24 | X2 – negative sequence reactance |  |  | p.u** | [9 empty] | 1
IV.25 | X0 – zero sequence reactance |  |  | p.u** | [9 empty] | 1
IV.26 | Generator Grounding | [12 empty] | 1
IV.27 |  | If grounded through impedance, please enter: | R: | ohms | [9 empty] | 2 | 139 | Grounded through Impedance
IV.28 |  |  | X: | ohms | [9 empty] | 2 | 139 | Grounded through Impedance
IV.29 | ** On generator MVA base and nominal line voltage (kV) Base
V. Inverter-Based Machine Information (Individual Inverter Data)
Inverter/Converter Data
V.1 | Will project be using a solar tracking system? If Yes, please provide a brief description of the tracking system to be used: | [12 empty] | 1
| Inverter Name |  |  |  | Gen Type1 |  | Gen Type2 | [6 empty] | 0 | calculation
V.2 | List of adjustable set points for the protective equipment or software | [12 empty] | 1
0
0
0
V.3 | Harmonics Characteristics | [12 empty] | 1
0
0
0
V.4 | Start-up Requirement | [12 empty] | 1
0
0
0
| Maximum design fault contribution current*: |  |  |  | Please complete short circuit data on "SCD Table" | [8 empty] | 0
0
0
0
0
0
V.9 | Does the inverter produce negative sequence fault current | [12 empty] | 1
V.10 | Will the inverter go into momentary cessation (i.e. connected to the grid but not injecting any current into the grid) during abnormal voltage conditions? | [12 empty] | 1
| If yes, fill out the following: | [12 empty] | 0
V.11 |  | Low voltage momentary cessation voltage threshold |  | p.u. | [9 empty] | 2 | 167 | Yes; explain below
V.12 |  | High voltage momentary cessation voltage threshold |  | p.u. | [9 empty] | 2 | 167 | Yes; explain below
V.13 |  | Time delay before the inverter begins injecting current after momentary cessation, once voltage has returned to within the momentary cessation voltage threshold(s) |  | seconds | [9 empty] | 2 | 167 | Yes; explain below
V.14 |  | Active current ramp rate when recovering from momentary cessation |  | p.u./sec | [9 empty] | 2 | 167 | Yes; explain below
V.15 |  | MVA base for the active current ramp rate above |  | MVA | [9 empty] | 2 | 167 | Yes; explain below
| If no, fill out the following: | [12 empty] | 0
V.16 |  | Describe inverter control during the system fault conditions. Provide information regarding control freeze, priority between active and reactive currents, master controller vs local control, etc. Include the voltage regulation propotional gain (k-factor) of the reactive current. | [11 empty] | 2 | 167 | No; explain below
0
0
0
V.17 |  | Does the inverter lock itself out after certain numbers of tripping during a given period? If yes, please describe the number of trips to lock-out and how the inverter restores operation. | [11 empty] | 2 | 167 | No; explain below
0
0
0
V.18 |  | Once tripped, what is the return ramp rate in %/second at what MVA base | [11 empty] | 2 | 167 | No; explain below
0
V.19 | Frequency tripping settings - provide up to 10 pairs of frequency tripping value and associated time delay; if no frequency tripping, please enter (57Hz, 999sec) and (63Hz, 999sec) |  |  | Hz, Sec | [9 empty] | 1
0
0
0
0
0
0
0
0
0
VI. Energy Storage Information
VI.1 | Select the source of charging ( transmission grid, on-site generator, etc.) |  |  |  |  | Tip: Select "transmission grid" if there are multiple charging sources inlcuding transmission grid. | [7 empty] | 1
VI.2 | If selected "other" above, explain | [12 empty] | 2 | 197 | other (please explain)
VI.3 | Select the operation of charging | [12 empty] | 1
| Storage Device Specification Data (Enter information at the device terminal) |  |  |  | Gen Type2 | [8 empty] | 1
VI.4 | Total Storage Capability |  |  | MWh | [9 empty] | 1
VI.5 | Charge/Discharge Cycle Efficiency |  |  | % | [9 empty] | 1
VI.6 | Rated Storage Discharging Power |  |  | MW | [9 empty] | 1
VI.7 | Discharge Duration under Rated Power |  |  | Hours | [9 empty] | 1
VI.8 | Maximum Storage Discharging Power |  |  | MW | [9 empty] | 1
VI.9 | Discharge Duration under Maximum Power |  |  | Hours | [9 empty] | 1
VI.10 | Rated Storage Charging Power |  |  | MW | [9 empty] | 1
VI.11 | Charge Duration under Rated Power |  |  | Hours | [9 empty] | 1
VI.12 | Maximum Storage Charging Power |  |  | MW | [9 empty] | 1
VI.13 | Charge Duration under Maximum Power |  |  | Hours | [9 empty] | 1
VI.14 | Requested Storage Charging Power (gross charging power to be studied at the terminal) |  |  | MW | [9 empty] | 1
| Primary frequency response operating range | [12 empty] | 0
VI.15 |  | Minimum State of Charge |  | % | [9 empty] | 1
VI.16 |  | Maximum State of Charge |  | % | [9 empty] | 1
VII. Voltage / Power Factor Control, Frequency Control & Power Plant Controller
Reactive Capability Requirements
|  | Synchronous Generators |  |  | The Generating Unit will maintain a composite power delivery at continuous rated power output at the terminals of the Electric Generating Unit at a power factor within the range of 0.95 leading to 0.90 lagging.
|  | Asynchronous Generators |  |  | The Generating Unit will maintain a composite power delivery at continuous rated power output at the high-side of the generator substation at a power factor within the range of 0.95 leading to 0.95 lagging. This power factor range standard shall be dynamic and can be met using, for example, power electronics designed to supply this level of reactive capability (taking into account any limitations due to voltage level, real power output, etc.) or fixed and switched capacitors or reactors, or a combination of the two. Refer to FERC Order No. 827 for more detail.
Devices to Provide Required Reactive Capability
VII.1 | 1) Reactive power capability from generators at the expected ambient temperture |  | Qmax | MVARS |  |  | For your reference, Qmax and Qmin to the right are calculate from the gross MVA and MW. You may enter any Qmax and Qmin within the calculated range. |  |  |  | 0 |  |  | 0
VII.2 |  |  | Qmin | MVARS | [6 empty] | 0 |  |  | 0
VII.3 | Expected ambient temperature for the reactive capability above |  |  | ⁰C | [9 empty] | 1
| 2) Additional reactive devices |  |  |  | Var Device 1 |  | Var Device 2 |  | Var Device 3 |  | Var Device 4
VII.4 |  |  | Type of Device | [10 empty] | 0 | 0 | 0
VII.5 |  |  | If other, please select static or dynamic and describe |  |  | 4 Stages |  | 4 Stages |  | 4 Stages |  | 4 Stages |  | 2 | 231 | Other (Explain Below)
VII.6 |  |  | Qmax | MVARS | [9 empty] | 1
VII.7 |  |  | Qmin | MVARS | [9 empty] | 1
VII.8 |  |  | Location | [10 empty] | 1
VII.9 | Total reactive capability |  | Qmax |  | 0
VII.10 |  |  | Qmin |  | 0
VII.11 | Total dynamic reactive capability |  | Qmax |  | 0
VII.12 |  |  | Qmin |  | 0
VII.13 | Estimated dynamic reactive capability requirement if asynchronous generators |  | Qmax |  | 0 | The calculated values are to help the IC to complete the IR form. The reactive capability requirement accounting for var losses will be determined in the interconnection studies.
VII.14 |  |  | Qmin |  | 0
Primary Frequency Response Requirements
| Requirement |  |  |  | Interconnection Customer is required to install a governor or equivalent controls with the capability of operating: (1) with a maximum 5 percent droop on the nameplate capacity base and +/-0.036Hz deadband; or (2) in accordance with the relevant droop, deadband, and timely and sustained response setteings form an approved NERC Reliability Standard providng for equivalent or more stringent paramenters.Refer to FERC Order 842 for more detail. | [8 empty] | 0
| Generator Name |  |  |  | Gen Type1 | Gen Type2 | [7 empty] | 0 | calcualted
VII.15 | Upward frequency response droop (increase output for low frequency) |  |  | % | [9 empty] | 1
VII.16 | Downward frequency response droop (reduce output for high frequency) |  |  | % | [9 empty] | 1
VII.17 | MW base for the droop above |  |  | MW | [9 empty] | 1
VII.18 | Frequency response deadband |  | +/- | Hz | [9 empty] | 1
Power Plant Controller
VII.19 | Is there a Power Plant Controller (PPC)? |  |  |  |  | If yes, please answer the followings VII.19 to VII.31 | [7 empty] | 1
VII.20 | PPC manufacturer | [12 empty] | 1
| PPC VOLTAGE/VAR CONTROL | [12 empty] | 0
VII.21 | Plant level voltage/Var control mode under continuous normal conditions |  |  |  |  | If other, please explain | [7 empty] | 2 | 252 | Yes
VII.22 | Plant level voltage/Var control mode under abnormal voltage conditions |  |  |  |  | If other, please explain | [7 empty] | 2 | 252 | Yes
VII.23 | Does the PPC freeze voltage/Var control at low voltage? | [12 empty] | 2 | 252 | Yes
VII.24 | If yes above, enter the voltage at which PPC freezes |  |  | p.u. | [9 empty] | 2 | 258 | Yes
VII.25 | Does the PPC implement voltage droop control? | [12 empty] | 2 | 253 | Yes
VII.26 | If yes above, enter the voltage droop |  |  | % | [9 empty] | 2 | 260 | Yes
VII.27 | Provide a general description of the control coordination among generators/inverters, reactive devices and transformer tap changers. | [12 empty] | 2 | 253 | Yes
0
0
| PPC FREQUENCY/MW CONTROL | [12 empty] | 0
VII.28 | Does the PPC controls overall primary frequency response capability |  |  |  |  | If yes, please answer the next question | [7 empty] | 2 | 253 | Yes
VII.29 | If yes above, will the PPC maintain headroom for upward frequency response (increasing output for low frequency)? | [12 empty] | 2 | 265 | Yes
VII.30 | Describe how the MW at Point of Interconnection is controlled. | [12 empty] | 2 | 253 | Yes
0
0
VII.31 | MW upward ramp rate limit (enter a positive number) |  |  | MW/min | [9 empty] | 2 | 253 | Yes
VII.32 | MW downward ramp rate limit (enter a negative number) |  |  | MW/min | [9 empty] | 2 | 253 | Yes
VIII. Transformer Data (GSU and pad-mount transformers)
| For each type of transformer, fill out the data form provided in the following table(s). Supply copy of nameplate and manufacture’s test report when available. | [12 empty] | 0 | 0 | 0
| Transformer Name |  |  |  | XFMR1 |  |  | XFMR2 |  |  | XFMR3 |  |  | 0 | 0 | 0
VIII.1 | No. of Transformers | [12 empty] | 1
VIII.2 | Phase | [12 empty] | 1
[5 empty] | H Winding | X Winding | Y Winding | H Winding | X Winding | Y Winding | H Winding | X Winding | Y Winding | 0
| RATING | [12 empty] | 0
VIII.3 | Rated MVA (Please enter the rating to model the transformer in the interconnection studies) |  |  | MVA | [9 empty] | 1
VIII.4 | Connection (Delta, Wye, Gnd.) | [12 empty] | 1
VIII.5 | Cooling Type (OA,OA/FA, etc.) | [12 empty] | 1
VIII.6 | Temperature Rise Rating |  |  | ⁰C | [9 empty] | 1
VIII.7 | Rated Voltage |  |  | kV | [9 empty] | 1
VIII.8 | BIL |  |  | kV | [9 empty] | 1
VIII.9 | Available Taps (% of rating) | [12 empty] | 0
VIII.10 | Load Tap Changer? (Yes or No) | [12 empty] | 1
VIII.11 | Tap Settings |  |  | % of rating | [9 empty] | 2 | 287 | Yes
0
| IMPEDANCE |  |  |  | H-X | H-Y | X-Y | H-X | H-Y | X-Y | H-X | H-Y | X-Y | 0
VIII.12 | Percent ( impedance Z) |  |  | % | [9 empty] | 1
VIII.13 | MVA Base |  |  | MVA | [9 empty] | 1
VIII.14 | Tested Taps | [12 empty] | 0
0
| WINDING RESISTANCE |  |  |  | H-X | H-Y | X-Y | H-X | H-Y | X-Y | H-X | H-Y | X-Y | 0
VIII.15 | X/R Ratio | [12 empty] | 1
Current Transformer Ratios
VIII.16 |  | H
VIII.17 |  | X
VIII.18 |  | Y
VIII.19 |  | N
Percent Exciting Current at:
VIII.20 |  | 100% voltage | [11 empty] | 1
VIII.21 |  | 110% voltage | [11 empty] | 1
VIII. Transformer Data (continued, pad-mount transformers only)
| For each type of transformer, fill out the data form provided in the following table(s). Supply copy of nameplate and manufacture’s test report when available. | [12 empty] | 0 | 0 | 0
| Transformer Name |  |  |  | XFMR4 |  |  | XFMR5 |  |  | XFMR6 |  |  | 0 | 0 | 0
VIII.1 | No. of Transformer | [12 empty] | 1
VIII.2 | Phase | [12 empty] | 1
[5 empty] | H Winding | X Winding | Y Winding | H Winding | X Winding | Y Winding | H Winding | X Winding | Y Winding | 0
| RATING | [12 empty] | 0
VIII.3 | Rated MVA |  |  | MVA | [9 empty] | 1
VIII.4 | Connection (Delta, Wye, Gnd.) | [12 empty] | 1
VIII.5 | Cooling Type (OA,OA/FA, etc.) | [12 empty] | 1
VIII.6 | Temperature Rise Rating |  |  | ⁰C | [9 empty] | 1
VIII.7 | Rated Voltage |  |  | kV | [9 empty] | 1
VIII.8 | BIL | [12 empty] | 1
VIII.9 | Available Taps (% of rating) | [12 empty] | 0
VIII.10 | Load Tap Changer? (Y or N) | [12 empty] | 1
VIII.11 | Tap Settings | [12 empty] | 2 | 321 | Yes
0
| IMPEDANCE |  |  |  | H-X | H-Y | X-Y | H-X | H-Y | X-Y | H-X | H-Y | X-Y | 0
VIII.12 | Percent |  |  | % | [9 empty] | 1
VIII.13 | MVA Base |  |  | MVA | [9 empty] | 1
VIII.14 | Tested Taps | [12 empty] | 0
0
| WINDING RESISTANCE |  |  |  | H-X | H-Y | X-Y | H-X | H-Y | X-Y | H-X | H-Y | X-Y | 0
VIII.15 | X/R Ratio | [12 empty] | 1
Current Transformer Ratios
VIII.16 |  | H
VIII.17 |  | X
VIII.18 |  | Y
VIII.19 |  | N
Percent Exciting Current at:
VIII.20 |  | 100% voltage | [11 empty] | 1
VIII.21 |  | 110% voltage | [11 empty] | 1
IX. Interconnection Facilities Line Data
There is no need to provide data for new lines that are to be planned by Westlands Water District. However, for transmission lines that are to be planned by the generation developer, please provide the following information:
IX.1 | Is the project sharing a gen-tie with other projects? | [12 empty] | 1
IX.2 |  | If yes, please specify the other project(s) and location on the gen-tie the project is Interconnecting to: | [11 empty] | 2 | 344 | Yes (See Below)
0
0
0
IX.3 | Is the project interconnection to an existing transmission line? | [12 empty] | 1
IX.4 |  | If yes, please specify the specific Point of Interconnection (POI) location on such transmission line, including the pole number(s). | [11 empty] | 2 | 349 | Yes (See Below)
0
0
0
[5 empty] | Line1 | Line 2 | Line 3 | Line 4 | Line5 | Line 6 | Line 7 | Line 8 | Line 9 | 0
IX.5 | Nominal Voltage |  |  | kV | 0 0: 0 | calculated
IX.6 | Line Length |  |  | Miles | bar: 0 0
IX.7a | Line Termination Point (From) |  |  | From: | bar: 0 0
IX.7b | Line Termination Point (To) |  |  | To: | bar: 0 0
If this is a new line planned by the IC and the line length is not negligible, completed the following:
IX.8 | Conductor Type
IX.9 | Conductor Size
If Bundled:
IX.10 |  | Number per Phase
IX.11 |  | Bundle Spacing |  | Inches
IX.12 | Phase Configuration
Phase Spacing:
IX.13 |  | A-B |  | Feet
IX.14 |  | B-C |  | Feet
IX.15 |  | C-A |  | Feet
IX.16 | Distance of lowest conductor to Ground at full load and 40 C |  |  | Feet
Ground Wire
IX.17 |  | Type
IX.18 |  | Size
IX.19 |  | Distance to Ground |  | Feet
Summer line ratings in amperes
IX.20 |  | Normal |  | Amps
IX.21 |  | Emergency |  | Amps
Summer line ratings in MVA (Calculation)
IX.22 |  | Normal |  | MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IX.23 |  | Emergency |  | MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Winter line ratings in amperes
IX.24 |  | Normal |  | Amps
IX.25 |  | Emergency |  | Amps
Winter line ratings in MVA (Calculation)
IX.26 |  | Normal |  | MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IX.27 |  | Emergency |  | MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IX.28 | Positive Sequence Resistance (R) (for entire line length) |  |  | p.u.**
IX.29 | Positive Sequence Reactance (X) (for entire line length) |  |  | p.u.**
IX.30 | Zero Sequence Resistance (R0) (for entire line length) |  |  | p.u.**
IX.31 | Zero Reactance (X0) (for entire line length) |  |  | p.u.**
IX.32 | Line Charging (B) |  |  | p.u.**
** On 100-MVA and nominal line voltage (kV) Base
| ACTION REQUIRED: |  | Please submit a Tower Configuration Diagram
X. For generators with a collector system, provide Collector System Equivalence Data
| Line |  |  |  | Collector 1 | Collector 2 | Collector 3 | Collector 4 | Collector 5 | Collector 6 | Collector 7 | Collector 8 | Collector 9
Provide values for each equivalence collector circuit at all voltage levels.
X.1 | Nominal Voltage |  |  | kV | 0 0: 0 | calculated
| Summer line ratings in Amperes |  |  |  | 0 0: 0
X.2 |  | Normal |  | Amps | bar: 0 0
X.3 |  | Emergency |  | Amps | bar: 0 0
| Summer line ratings in MVA (Calculation) |  |  |  | 0 0: 0
X.4 |  | Normal |  | MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X.5 |  | Emergency |  | MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Winter line ratings in Amperes |  |  |  | 0 0: 0
X.6 |  | Normal |  | Amps | bar: 0 0
X.7 |  | Emergency |  | Amps | bar: 0 0
| Winter line ratings in MVA (Calculation) |  |  |  | 0 0: 0
X.8 |  | Normal |  | MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X.9 |  | Emergency |  | MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X.10 | Positive Sequence Resistance (R1) (for entire line length of each collector circuit) |  |  | p.u.** | bar: 0 0
X.11 | Positive Sequence Reactance (X1) (for entire line length of each collector circuit) |  |  | p.u.** | bar: 0 0
X.12 | Zero Sequence Resistance (R0) (for entire line length of each collector circuit) |  |  | p.u.** | bar: 0 0
X.13 | Zero Reactance (X0) (for entire line length of each collector circuit) |  |  | p.u.** | bar: 0 0
X.14 | Line Charging (B) (for entire line length of each collector circuit) |  |  | p.u.** | bar: 0 0
** On 100-MVA and nominal line voltage (kV) Base
XI. Load Flow and Dynamic Models
(to be provided via electronic submission):
| Provide load flow model for the generating plant and its interconnection facilities in GE PSLF *.epc format, including new buses, generators, transformers, interconnection facilities. One copy of this data should be provided via electronic submission. An equivalent model is required for the plant with generation collector systems. This data should reflect the technical data provided in this Attachment A. |  |  |  | Line5: Please use "Power Flow Model" and "Dynamic Model" to create the .epc and .dyd files.
For each generator, governor, exciter and power system stabilizer, select the appropriate dynamic model from the General Electric PSLF Program Manual and provide the required input data. For inverter based generating facilities, select the appropriate generator and control models from the General Electric PSLF Program Manual and provide the required input data. For each generator that will activate voltage/frequency relaying, provide appropriate dynamic models for low/high voltage/frequency ride-through that comply with NERC standard PRC-029-1. The latest WECC approved model must be used. Provide a completed *.dyd file that contains the information specified in this section. One copy of this data should be provided via electronic submission.
If you require assistance in developing the models, we suggest you contact General Electric. Accurate models are important to obtain accurate study results. Costs associated with any changes in facility requirements that are due to differences between model data provided by the generation developer and the actual generator test data, may be the responsibility of the generation developer.
For information regarding GE PSLF and its model library, please send an email to pslf-caiso@ge.com

## SCD Table
Short Circuit Performance Table for Inverter Based Generators
Generating Facility Name |  |  | Fault Type |  | Generating Facility Name |  |  | Fault Type |  | Generating Facility Name |  |  | Fault Type
Positive Sequence Voltage (pu) | Positive Sequence Current (pu) | Negative Sequence Current (pu) | Positive Sequence Power Factor Angle (deg) | Negative Sequence Power Factor Angle (deg) | Positive Sequence Voltage (pu) | Positive Sequence Current (pu) | Negative Sequence Current (pu) | Positive Sequence Power Factor Angle (deg) | Negative Sequence Power Factor Angle (deg) | Positive Sequence Voltage (pu) | Positive Sequence Current (pu) | Negative Sequence Current (pu) | Positive Sequence Power Factor Angle (deg) | Negative Sequence Power Factor Angle (deg)
1 Cycle Time Frame |  |  |  |  | 1 Cycle Time Frame |  |  |  |  | 1 Cycle Time Frame
0.9 |  |  |  |  | 0.9 |  |  |  |  | 0.9
0.8 |  |  |  |  | 0.8 |  |  |  |  | 0.8
0.7 |  |  |  |  | 0.7 |  |  |  |  | 0.7
0.6 |  |  |  |  | 0.6 |  |  |  |  | 0.6
0.5 |  |  |  |  | 0.5 |  |  |  |  | 0.5
0.4 |  |  |  |  | 0.4 |  |  |  |  | 0.4
0.3 |  |  |  |  | 0.3 |  |  |  |  | 0.3
0.2 |  |  |  |  | 0.2 |  |  |  |  | 0.2
0.1 |  |  |  |  | 0.1 |  |  |  |  | 0.1
3 Cycle Time Frame |  |  |  |  | 3 Cycle Time Frame |  |  |  |  | 3 Cycle Time Frame
0.9 |  |  |  |  | 0.9 |  |  |  |  | 0.9
0.8 |  |  |  |  | 0.8 |  |  |  |  | 0.8
0.7 |  |  |  |  | 0.7 |  |  |  |  | 0.7
0.6 |  |  |  |  | 0.6 |  |  |  |  | 0.6
0.5 |  |  |  |  | 0.5 |  |  |  |  | 0.5
0.4 |  |  |  |  | 0.4 |  |  |  |  | 0.4
0.3 |  |  |  |  | 0.3 |  |  |  |  | 0.3
0.2 |  |  |  |  | 0.2 |  |  |  |  | 0.2
0.1 |  |  |  |  | 0.1 |  |  |  |  | 0.1
5 Cycle Time Frame |  |  |  |  | 5 Cycle Time Frame |  |  |  |  | 5 Cycle Time Frame
0.9 |  |  |  |  | 0.9 |  |  |  |  | 0.9
0.8 |  |  |  |  | 0.8 |  |  |  |  | 0.8
0.7 |  |  |  |  | 0.7 |  |  |  |  | 0.7
0.6 |  |  |  |  | 0.6 |  |  |  |  | 0.6
0.5 |  |  |  |  | 0.5 |  |  |  |  | 0.5
0.4 |  |  |  |  | 0.4 |  |  |  |  | 0.4
0.3 |  |  |  |  | 0.3 |  |  |  |  | 0.3
0.2 |  |  |  |  | 0.2 |  |  |  |  | 0.2
0.1 |  |  |  |  | 0.1 |  |  |  |  | 0.1
Generating Facility Name |  |  | Fault Type |  | Generating Facility Name |  |  | Fault Type |  | Generating Facility Name |  |  | Fault Type
Positive Sequence Voltage (pu) | Positive Sequence Current (pu) | Negative Sequence Current (pu) | Positive Sequence Power Factor Angle (deg) | Negative Sequence Power Factor Angle (deg) | Positive Sequence Voltage (pu) | Positive Sequence Current (pu) | Negative Sequence Current (pu) | Positive Sequence Power Factor Angle (deg) | Negative Sequence Power Factor Angle (deg) | Positive Sequence Voltage (pu) | Positive Sequence Current (pu) | Negative Sequence Current (pu) | Positive Sequence Power Factor Angle (deg) | Negative Sequence Power Factor Angle (deg)
1 Cycle Time Frame |  |  |  |  | 1 Cycle Time Frame |  |  |  |  | 1 Cycle Time Frame
0.9 |  |  |  |  | 0.9 |  |  |  |  | 0.9
0.8 |  |  |  |  | 0.8 |  |  |  |  | 0.8
0.7 |  |  |  |  | 0.7 |  |  |  |  | 0.7
0.6 |  |  |  |  | 0.6 |  |  |  |  | 0.6
0.5 |  |  |  |  | 0.5 |  |  |  |  | 0.5
0.4 |  |  |  |  | 0.4 |  |  |  |  | 0.4
0.3 |  |  |  |  | 0.3 |  |  |  |  | 0.3
0.2 |  |  |  |  | 0.2 |  |  |  |  | 0.2
0.1 |  |  |  |  | 0.1 |  |  |  |  | 0.1
3 Cycle Time Frame |  |  |  |  | 3 Cycle Time Frame |  |  |  |  | 3 Cycle Time Frame
0.9 |  |  |  |  | 0.9 |  |  |  |  | 0.9
0.8 |  |  |  |  | 0.8 |  |  |  |  | 0.8
0.7 |  |  |  |  | 0.7 |  |  |  |  | 0.7
0.6 |  |  |  |  | 0.6 |  |  |  |  | 0.6
0.5 |  |  |  |  | 0.5 |  |  |  |  | 0.5
0.4 |  |  |  |  | 0.4 |  |  |  |  | 0.4
0.3 |  |  |  |  | 0.3 |  |  |  |  | 0.3
0.2 |  |  |  |  | 0.2 |  |  |  |  | 0.2
0.1 |  |  |  |  | 0.1 |  |  |  |  | 0.1
5 Cycle Time Frame |  |  |  |  | 5 Cycle Time Frame |  |  |  |  | 5 Cycle Time Frame
0.9 |  |  |  |  | 0.9 |  |  |  |  | 0.9
0.8 |  |  |  |  | 0.8 |  |  |  |  | 0.8
0.7 |  |  |  |  | 0.7 |  |  |  |  | 0.7
0.6 |  |  |  |  | 0.6 |  |  |  |  | 0.6
0.5 |  |  |  |  | 0.5 |  |  |  |  | 0.5
0.4 |  |  |  |  | 0.4 |  |  |  |  | 0.4
0.3 |  |  |  |  | 0.3 |  |  |  |  | 0.3
0.2 |  |  |  |  | 0.2 |  |  |  |  | 0.2
0.1 |  |  |  |  | 0.1 |  |  |  |  | 0.1
Generating Facility Name |  |  | Fault Type |  | Generating Facility Name |  |  | Fault Type |  | Generating Facility Name |  |  | Fault Type
Positive Sequence Voltage (pu) | Positive Sequence Current (pu) | Negative Sequence Current (pu) | Positive Sequence Power Factor Angle (deg) | Negative Sequence Power Factor Angle (deg) | Positive Sequence Voltage (pu) | Positive Sequence Current (pu) | Negative Sequence Current (pu) | Positive Sequence Power Factor Angle (deg) | Negative Sequence Power Factor Angle (deg) | Positive Sequence Voltage (pu) | Positive Sequence Current (pu) | Negative Sequence Current (pu) | Positive Sequence Power Factor Angle (deg) | Negative Sequence Power Factor Angle (deg)
1 Cycle Time Frame |  |  |  |  | 1 Cycle Time Frame |  |  |  |  | 1 Cycle Time Frame
0.9 |  |  |  |  | 0.9 |  |  |  |  | 0.9
0.8 |  |  |  |  | 0.8 |  |  |  |  | 0.8
0.7 |  |  |  |  | 0.7 |  |  |  |  | 0.7
0.6 |  |  |  |  | 0.6 |  |  |  |  | 0.6
0.5 |  |  |  |  | 0.5 |  |  |  |  | 0.5
0.4 |  |  |  |  | 0.4 |  |  |  |  | 0.4
0.3 |  |  |  |  | 0.3 |  |  |  |  | 0.3
0.2 |  |  |  |  | 0.2 |  |  |  |  | 0.2
0.1 |  |  |  |  | 0.1 |  |  |  |  | 0.1
3 Cycle Time Frame |  |  |  |  | 3 Cycle Time Frame |  |  |  |  | 3 Cycle Time Frame
0.9 |  |  |  |  | 0.9 |  |  |  |  | 0.9
0.8 |  |  |  |  | 0.8 |  |  |  |  | 0.8
0.7 |  |  |  |  | 0.7 |  |  |  |  | 0.7
0.6 |  |  |  |  | 0.6 |  |  |  |  | 0.6
0.5 |  |  |  |  | 0.5 |  |  |  |  | 0.5
0.4 |  |  |  |  | 0.4 |  |  |  |  | 0.4
0.3 |  |  |  |  | 0.3 |  |  |  |  | 0.3
0.2 |  |  |  |  | 0.2 |  |  |  |  | 0.2
0.1 |  |  |  |  | 0.1 |  |  |  |  | 0.1
5 Cycle Time Frame |  |  |  |  | 5 Cycle Time Frame |  |  |  |  | 5 Cycle Time Frame
0.9 |  |  |  |  | 0.9 |  |  |  |  | 0.9
0.8 |  |  |  |  | 0.8 |  |  |  |  | 0.8
0.7 |  |  |  |  | 0.7 |  |  |  |  | 0.7
0.6 |  |  |  |  | 0.6 |  |  |  |  | 0.6
0.5 |  |  |  |  | 0.5 |  |  |  |  | 0.5
0.4 |  |  |  |  | 0.4 |  |  |  |  | 0.4
0.3 |  |  |  |  | 0.3 |  |  |  |  | 0.3
0.2 |  |  |  |  | 0.2 |  |  |  |  | 0.2
0.1 |  |  |  |  | 0.1 |  |  |  |  | 0.1
Generating Facility Name |  |  | Fault Type |  | Generating Facility Name |  |  | Fault Type |  | Generating Facility Name |  |  | Fault Type
Positive Sequence Voltage (pu) | Positive Sequence Current (pu) | Negative Sequence Current (pu) | Positive Sequence Power Factor Angle (deg) | Negative Sequence Power Factor Angle (deg) | Positive Sequence Voltage (pu) | Positive Sequence Current (pu) | Negative Sequence Current (pu) | Positive Sequence Power Factor Angle (deg) | Negative Sequence Power Factor Angle (deg) | Positive Sequence Voltage (pu) | Positive Sequence Current (pu) | Negative Sequence Current (pu) | Positive Sequence Power Factor Angle (deg) | Negative Sequence Power Factor Angle (deg)
1 Cycle Time Frame |  |  |  |  | 1 Cycle Time Frame |  |  |  |  | 1 Cycle Time Frame
0.9 |  |  |  |  | 0.9 |  |  |  |  | 0.9
0.8 |  |  |  |  | 0.8 |  |  |  |  | 0.8
0.7 |  |  |  |  | 0.7 |  |  |  |  | 0.7
0.6 |  |  |  |  | 0.6 |  |  |  |  | 0.6
0.5 |  |  |  |  | 0.5 |  |  |  |  | 0.5
0.4 |  |  |  |  | 0.4 |  |  |  |  | 0.4
0.3 |  |  |  |  | 0.3 |  |  |  |  | 0.3
0.2 |  |  |  |  | 0.2 |  |  |  |  | 0.2
0.1 |  |  |  |  | 0.1 |  |  |  |  | 0.1
3 Cycle Time Frame |  |  |  |  | 3 Cycle Time Frame |  |  |  |  | 3 Cycle Time Frame
0.9 |  |  |  |  | 0.9 |  |  |  |  | 0.9
0.8 |  |  |  |  | 0.8 |  |  |  |  | 0.8
0.7 |  |  |  |  | 0.7 |  |  |  |  | 0.7
0.6 |  |  |  |  | 0.6 |  |  |  |  | 0.6
0.5 |  |  |  |  | 0.5 |  |  |  |  | 0.5
0.4 |  |  |  |  | 0.4 |  |  |  |  | 0.4
0.3 |  |  |  |  | 0.3 |  |  |  |  | 0.3
0.2 |  |  |  |  | 0.2 |  |  |  |  | 0.2
0.1 |  |  |  |  | 0.1 |  |  |  |  | 0.1
5 Cycle Time Frame |  |  |  |  | 5 Cycle Time Frame |  |  |  |  | 5 Cycle Time Frame
0.9 |  |  |  |  | 0.9 |  |  |  |  | 0.9
0.8 |  |  |  |  | 0.8 |  |  |  |  | 0.8
0.7 |  |  |  |  | 0.7 |  |  |  |  | 0.7
0.6 |  |  |  |  | 0.6 |  |  |  |  | 0.6
0.5 |  |  |  |  | 0.5 |  |  |  |  | 0.5
0.4 |  |  |  |  | 0.4 |  |  |  |  | 0.4
0.3 |  |  |  |  | 0.3 |  |  |  |  | 0.3
0.2 |  |  |  |  | 0.2 |  |  |  |  | 0.2
0.1 |  |  |  |  | 0.1 |  |  |  |  | 0.1

## List (hidden)
Yes/No | Yes/No | Substation Name | Voltage Level | Gen Technology | Gen Type | Phase | Connection | Source of Charging | Operation of Charging | Type of VAR Device | Static/Dynamic | Plant Level Control Mode | Connection | Phase Configuration | Fault Type
Yes | Yes (See Below) | VCIP Substation No. 1-Newpoint | 500 | Induction | photovoltaic | Single Phase | Delta | transmission grid | follow BAA dispatch instructions | Fixed Capacitor | static | Power Factor Control Mode | Wye | Vertical | 3LG
No | No | VCIP Substation No. 2 | 230 | Synchronous | energy storage (battery) | Three Phase | Grounded WYE | AC-side on-site generator only |  | SVD | dynamic | Voltage Control Mode | Wye Grounded | Horizontal | SLG
N/A |  | VCIP Substation No. 3 |  | DC with Inverter |  |  | Ungrounded WYE | DC-side charging only |  | SVC |  | Reactive Power Control Mode | Delta | Triangular | LL
|  | VCIP Substation No. 4 |  | Doubly Asynchronous |  |  | Impedance Grounded | other (please explain) |  | Statcom |  | Coordinated Voltage and Q Control Mode | Delta (Buried)
|  | VCIP Substation No. 5 | [7 empty] | Other (Explain Below) |  | Other